How much protection do
FCC Part 15 Conducted Noise Limits Provide?
Will your radio work at your EOC?
Gordon Gibby MD
KX4Z NCS521
February 2024 / TECHCON 10

---
Goal
- Provide guidance to facility designers so that incidental or unintentional radiators will not disrupt or hamper backup High Frequency (HF) radio communications by radiating noise.
- Answer the question of whether advertised compliance with FCC Part 15 conducted noise limits is sufficient protection.

---
HF Backup Communications
- Dangerous world.
- Public switched telecommunications have multiple vulnerabilities not only to weather, but also to malicious intent of hackers or state actors
- HF communications are infrastructure-independent.
- Government, military and private entities therefore often use HF as a backup.

---
- Examples include Florida Division of Emergency Management using federally provided SHARES frequencies / log-periodic and loop antenna for backup communications to Florida Counties
- Military using NVIS and other communications for battlefield communications
- Traditional backup Embassy long-range communications.
- Recent interest by stockbrokers for decreased latency communications.

---
- Damage to HF backup communications can severely hamper coordination and control in the event that normal communications are overloaded or damaged.
- Examples include Katrina, Iowa derecchos and many more instances where weather degraded normal comms, misaligned microwave antennas, downed towers, or fire engulfed facilities.

---
Path Budget
- HF communications may be operating at the tail end of the allowable path budget.
- Adding 10dB of noise beyond background can be extremely disruptive to HF communications.

---
Unavoidable Noise

---
FCC Limits
- Above 30MHz Part 15 (and European CISPR regulations) require measurement of RADIATED noise.
- Below 30 MHz, only conducted noise is regulated.
- Why?

---
Inefficient Radiators
- Conventional engineering wisdom: antenna < 1/6 wavelength is inefficient
- Primary radiator of many devices is their power cord, which is short.
- Building wiring is highly variable and cannot be specified.
- Therefore, the only known radiator (power cord) is inefficient.
- More effective to limit the CONDUCTION of noise into that wiring, which will limit the power available to the (unknown) eventual building wiring.

---
FCC Conducted Noise Limits
Class B = residential; Class A = commercial, etc.

---
Alachua County
- Existing EOC has tremendous RF noise detected inside, on the roof, on the ground wiring, and everywhere throughout, presumably from computers and switching backup supplies.
- This necessitated very long coaxial cable runs to place antennas at good distances from the building.
- County is renovating a structure for a new EOC and proposes to put in uninterruptible power supplies potentially re-creating the problem.

---
Need to be able to advise designers now to specify equipment and installations that will NOT recreate the problem.

---
Device Under Test
3400 Watt Dual Fuel (Propane/Gasoline) inverter-based generator advertising Class B compliance.

---
Known Noise Maker
Our team has considerable experience with this inverter generator (and others) and knows that extensive filtering (>50dB) is required to allow it to operate in the neighborhood of HF antennas. (Despite Class B rating)
REFERENCE: https://cdn.automationdirect.com/static/manuals/emifilters/MIF23.pdf
“Filter Insertion Loss Characteristics, CISPR 17 – 50 Ohm method”

---
METHOD
Conducted Noise Measurement

---
V-type LISN constructed

---
Purpose of FCC-required LISN
- In case of device requiring AC power, prevents noise from AC lines reaching device and contaminating test.
- Provides 50 ohm load for frequencies of interest to device
- Provides separating impedance (50 uH) thought to simulate 30meters of house wiring.
- These devices are extremely $$$$

---
- Monitor Tap: 0.01uF cap instead of 0.1 (easily handles lowest frequency of interest)
- High Pass Filter (500kHz) added to reduce overloading of spectrum analyser by lower order harmonics (distortion) of the inverter output as not concerned by those.
- Sufficient external 50 ohm pad attenuators used to allow analyzer to operate.
- Measurements at 3.5, 7, 10.1 MHz. 10 kHz BW (nearest available to 9kHz standard)

---
Adequacy of LISN assessed by measuring SWR from the “hot” side.
- NOISE MEASUREMENT – combined differential + common mode measured from both hot and neutral wiring from generator versus ground.
- Generator GROUNDED by approx 5 foot #14 wire directly to solid ground rod.
- Note this is DIFFERENT from FCC prescribed measurement (DUT on 80cm high table, grounded only through cable, ground plane underneath)

---
Radiated Noise Measurement

---
- Not-to-Scale approximate physical setup.
- When appropriate, generator powers 2nd floor and portions of 1st floor

---
Antenna
- Non-resonant antenna approx 100 feet long
- 300 ohm window line to T tuner
- Assumption made that antenna is “full sized” for each band.

---
- At each frequency, manual T-type antenna tuner set for SWR<= 1.5:1
- Measurement of received energy taken at 3.5, 7, 10.1 MHz @ 10kHz Bandwidth
- Noise floor of spectrum analyser measured
- Baseline received without generator.
- Measurement with generator powering house.

---
Relevant RF Equations

---
AF for full size dipole

---
RESULTS
Assessment of adequate of home constructed LISN

---
Conducted Noise Measurements

---
Conducted Noise in FCC Units

---
Received Noise

---
DISCUSSION

---
- Grounding and generator placement enhanced radiation – but are prudent and normal expected safety procedures
- Generator is 6 years old.
- LISN data suggest adequate performance of LISN
- Background RF measurements fall nicely of RSGB data between “Rural” and “Quiet Rural” suggesting appropriateness of AF

---
Background noise measured

---
Passive Environment
- Key understanding that the environment is LINEAR. ie. Doubling noise radiated will double noise received.
- Therefore all results can be linearly scaled down to “control background” to find the necessary limit on ACTUAL conducted noise to avoid hampering RF reception.

---
Computation of Required Performance

---
Illustrative Results

---
This one anecdotal situation:
- Stated compliance with FCC limits – even Class B limits – is NOT ENOUGH
- ACTUAL performance in realistic situation is far more important.
- 80 meters: Req. 9DB below Class A or meet Class B
- 40 meters: Req actually meeting either A or B
- 30 meters: Req actually under Class A by 11 dB or under Class B by 1 dB

---
- Only one situation studied.
- Actual performance far more important than contrived laboratory claims
- Inadequate performance can be salvaged by
  - Pre filtering with industrial filters safely mounted
  - Prefiltering with some consumer filters available

---
https://www.digikey.com/en/products/detail/qualtek/849-20%2F004/1680215
https://www.apc.com/us/en/product/C2/apc-av-c-type-2-outlet-wall-mount-power-filter-120v

---
https://tripplite.eaton.com/isobar-2-outlet-surge-protector-direct-plug-in-1410-joules-3-leds-black-housing-5-in-height~ULTRABLOK

---
Consequences of failure to protect
- Hampered communications at all times
- Volunteers will be acutely aware
- Facility will be judged substandard
- Attrition of volunteers
- Resulting loss of federal “match”
- Lack of capability when needed

---
Questions / Comments?

---
Thank You!